Draft Trip Report

UKRAINE STEAM PARTNERSHIP:

Workshop on International experience of energy efficiency improvements of generation and consumption of heat in steam systems

January 16 – 19th, 2000, Kiev, Ukraine.
For

THE ALLIANCE TO SAVE ENERGY 

1200 18th Street, NW, Suite 900, Washington, DC 20036.  202-857-0666.  Fax:202-331-9588

Prepared By

Gurvinder Singh

Industrial Energy Efficiency Expert

February 15, 2000

PREFACE

The work described in this trip report was carried out by Mr. Gurvinder Singh within the framework of the U.S. Department of Energy (USDOE) Ukraine Steam Partnership program, under contract to Alliance to Save Energy.

This report summarizes the in-country activities of Mr. Gurvinder Singh during his trip to Kiev, Ukraine from January 16th to 21st, 2000.  The author would like to acknowledge the assistance of Mr. David Jaber of the Alliance to Save Energy, Washington DC, who assisted in collecting valuable information for the use in the workshop, and Messrs. Artem Kharchenko, Andriy Vasylego of the Alliance office in Kiev and Mr. Alexander Gloukhov who manages Alliance activities in Russia for translating the workshop materials into Russian.

INTRODUCTION

The Ukraine Steam Partnership program is designed to implement energy efficiency improvements in industrial steam systems. These improvements are to be made by the private plants and local government departments responsible for generation and delivery of energy to end-users.  One of the activities planned under this program was to provide a two-day training workshop on industrial steam systems focusing on energy efficiency issues related to the generation, distribution, and consumption of steam. The workshop was geared towards plant managers, who are not only technically oriented, but are also key decision makers in their respective companies.

The Agency for Rational Energy Use and Ecology (ARENA-ECO), a non-governmental, not-for-profit organization founded to promote energy efficiency and environmental protection in Ukraine, in conjunction with the Alliance staff in Kiev sent out invitations to potential participants in all the regions of Ukraine.  Approximately 32 participants signed up for the workshop (Appendix 1) representing all of the major regions of Ukraine in a diverse range of industrial sectors.

(Note: In Appendix 1, delete the comments column and describe what each company is; some companies have names, but no descriptions)

The purpose of this report is the describe the proceedings from the workshop and provide recommendations from the workshop’s roundtable discussion. 
The workshop was broken down into two main areas:

· Energy efficient boiler house steam generation

· Energy efficient steam distribution and consumption

The workshop also covered the following topics. 

· Ukrainian boilers

· Water treatment systems

· A profile of UKRESCO (Ukrainian Energy Services Company)

· Turbine expanders and electricity generation

· Enterprise energy audit basics

· Experience of steam use in Donetsk oblast

Mr. Gurvinder Singh prepared and presented the boiler steam generation portion of the workshop. Representatives from Armstrong International SA, Mr. Alexander Zygmuntowicz, Sales Manager for Eastern Europe and CIS, and Mr. Petrovich Soshnikov, a local representative in Ukraine, presented opportunities for saving energy in steam distribution and consumption of industrial operations.  Local representatives from various other organizations made the remaining presentations, which covered the types of efficient steam system technologies currently available on the Ukrainian market and how these technologies can help solve common energy efficiency problems. 

A day prior to the workshop, Mr. Gurvinder Singh met with the ARENA-ECO translators to discuss the main points of the presentations and to clarify the appropriate Ukrainian translation for some of the difficult and unfamiliar technical terms used in the presentation materials.  Mr. Singh also met with the Armstrong team to ensure that the two presentations would not overlap. The following steps were taken to support the portion of the workshop related to boilers: 

· All presentation materials were translated into Russian.
· A copy of the overheads translated into Russian was handed out to each of the workshop participants.
· Literature in Russian on boiler equipment from a U.S. boiler manufacturer (Cleaver-Brooks) was distributed to each participant.
The workshop was held at ARENA-ECO’s offices on January 18th and 19th, 2000.  The workshop was opened with a welcome address by Mr. Mykola Raptsun, President of ARENA-ECO, followed by a welcome and opening remarks by Mr. Tom Lemley, Resident Advisor of the Alliance to Save Energy in Ukraine. 

Mr. Gurvinder Singh gave six presentations over the two days:

· Introduction to industrial boiler energy use in Ukraine and the U.S.

· Basic overview of boiler efficiency and combustion controls.

· Combustion efficiency improvements: boiler tune-up/maintenance.

· Combustion efficiency improvements: high efficiency burner systems and controls and stack heat recovery economizers.

· Metering equipment and insulation systems.

· Chemical treatment and blowdown heat recovery.

The overheads for these presentations are included in appendices 3-8.

PARTICIPANT QUESTIONNAIRE EVALUATION

 Prior to the workshop, Mr. Gurvinder Singh gave the workshop participants a questionnaire. The purpose of this questionnaire was to collect information on the boiler types, sizes and existing energy efficiency practices to help tailor future workshops on boiler systems to the most prevalent boiler systems. A copy of the questionnaire is included in Appendix 9.

It is important to acknowledge that the original intent was to have the questionnaire completed before any boiler presentations were made; however, since some time was lost in the beginning of the workshop, the presentation material was given priority over the questionnaire.  Thus, the answers to questions relating to energy efficiency (Question Nos. 9 and 10) may not be considered objective.  Most of the answers reflect the topics that were covered in the boiler presentations.

Also, the number of responses to each question varies as not all questions were answered by all the participants.  Therefore, it is difficult to establish correlation between the answers to the various questions.  Thus, the answers can and should be interpreted keeping in mind the limitations.

In general, based on answers in the questionnaire and further discussion with workshop participants, the boiler characteristics for the plants represented at the workshop were as follows:

· The boiler operating pressure ranged from 200 psig upwards.

· The reported efficiency was generally near the mid-80s.  The convention in Ukraine, as in Western Europe, is to use lower heating value (LHV) in calculating the energy efficiency.  In the U.S., the convention is to use higher heating values (HHV), which result in equivalent energy efficiencies 6 to 11 percent lower then the Ukrainian boilers.  Thus, the reported efficiencies when corrected to U.S. standard are mid-70s to 80, indicating that there is significant room for energy efficiency improvements.

· The average load numbers were hard to interpret, as the respondents did not specify whether the load was the average per boiler or for the total battery of boilers.

· The reported stack temperatures were very low.  These are temperatures that are typically observed in systems that have economizer heat recovery systems.  Based on the author of this report’s prior experience of working in Ukrainian plants, these numbers appear very optimistic.

· The most common fuels were natural gas and mazout (No. 6 fuel oil).  There were no boilers operated on coal.  Although coke gas was reported, this was only used at the steel plants represented at the workshop.

· The level of excess air reported is not reliable as this topic was discussed in detail at the workshop and is likely to have biased the answer.  Most respondents to the questionnaire answered that excess air levels were below 20 percent.

· The resources used to obtain information on operating boilers efficiently provide valuable insights.  The resource used most was the one with the  lowest score, since 1 was designated for used most and 5 stood for used least.  The responses yielded the following results:

· Guidelines from government agencies (Average score 1.83)

· Boiler Inspector (Average score 2.28)

· Boiler Manufacturer’s Guidelines (Average score 2.62)

· Boiler Operator Experience (Average score 3.12)

The boiler water treatment is handled by a separate department than the boiler operation department.  There is a high probability that there is a communication gap between the boiler operation staff and the water treatment staff. It is likely that water treatment needs are not well established and could lead to improved operation.

INSIGHTS FROM ROUNDTABLE DICUSSION WITH PARTICIPANTS
Mr. Sergei Surnin, Executive Director of ARENA-ECO, led a roundtable discussion at the conclusion of the workshop.   In general, the participants were enthusiastic about the workshop. The participants did provide some useful comments and suggestions for future workshops, which are outlined below. 

· One participant suggested that more information on metering equipment be included in future workshops, due to the lack of good metering equipment available locally for industrial applications.

· There was also a suggestion to include hot water boiler systems in addition to steam boilers.

Other general comments were:

· Incorporate refrigerant and cooling systems into the workshop agenda.

· Increase the diversity of industry represented at the workshops.

· Target college level students to get them thinking about energy efficiency early in their careers.

· Provide more information on valves, as there are no good quality valves available in Ukraine.

 CONCLUSIONS AND RECOMMENDATIONS 

The steam and boiler workshop was well received; however, based on the questionnaire and feedback, the following recommendations are made regarding future workshops:

· The boiler materials were based on gas and oil fired boilers.  These seem to be appropriate for Ukraine, as these fuels are the most common representative fuels used in Ukraine’s industrial facilities.

· The main energy efficiency areas that were covered in this workshop are appropriate based on the reported efficiency levels.  However, in future workshops, the main areas that can be addressed are combustion efficiency and water treatment/blowdown.

· Based on the response to the question of where the plant personnel receive their boiler energy efficiency data, there seems to be need for further research and investigation into the quality of the most commonly referenced resource for such data:  government guidelines.  The participants reported that they get their information from government guidelines followed by boiler inspectors.  The boiler inspectors are most likely enforcing the government guidelines, although this is a speculation derived from the limited data we have from the questionnaire.  It is recommended that these guidelines be obtained and evaluated, which is a task that will be proposed in a second year work plan for the Ukraine Steam Partnership.   It is possible that the guildelines may be outdated, therefore it is necessary to update them to reflect the current technologies and practices, both considering what is presently available on the Ukrainian market and what corresponds to European and other Western standards.  A carefully updated edition of the guidelines, as a joint effort of Ukrainian and Western experts, may be a good way to influence the boiler room practices in Ukrainian industries.

·  It is conceivable there is a communication gap between the boiler operator and the boiler water treatment team.  This must be studied to verify if indeed there is a gap.  If a gap exists then the appropriate measures should be taken to better integrate the water treatment and boiler operation practices.

*****

Appendix 1

List of Participants

LIST of PARTICIPANTS

Steam Efficiency Workshop

January 18-19, 2000 Kyiv

No
Name
Company
Comments

1
2
3
4

1
Michael Boyko 

Deputy Chief Powerman
Armyansk,

JSC «TYTAN»


2
Oleg Bezsmertny

Inspector
Sumy,

State Energy Conservation Inspection


3
Volodimir Vyfanyk 

Deputy Chief Designer 
Monastyrysche

JSC «ТЕKОМ»


4
Ivan Grygoryev 

Chief Engineer 
Romny

Milk Plant


5
Valery Dubenko 

Chief Powerman
Donetsk

А.В.К.


6
Dmytro Eremenko

Chief Powerman
Mariupol

Sea port


7
Gennady Genylo 

Deputy Chief Engineer
Mariupol

Bakery plant


8
Alexander Zenkov

Chief Powerman
Krasnoperekopsk,

JSC «Crimea soda  plant»


9
Valery Zynovyev 

Engineer
Donetsk

JSV «А.В.К.»


10
Victor Yschenko, 

Deputy Chief Powerman
Dniprodzherzynsk,

Coke plant


11
Alexander Kyrichok, 

Head of Inspection Department
Donetsk,

State Energy Conservation Inspection


12
Mykola Kytaev Кітаєв 

Deputy of the Head of Inspection Department
Mariupol,

State Energy  Conservation Inspection


13
Mykola Korgyk, 

President
Ivano-Frankivsk

ESCO West


14
Sergey Korolyov, 

Engineer
Sumy

“OilGasTechnology”


15
Taras Levytsky

Head of the Boiler House
Mykolayiv

Brewery «Yantar»


1
2
3
4

16
Victor Mykhaylichenko

Chief Engineer
Mykolayiv

Alumina plant


17
Victor Mykhaylovksy

Director
Kyiv

ЕНВІТЕК


18
Vasyl Movchan

Head of the Department
Sumy

Chemical Plant


19
Alexander Novoseltsev

Menager
Kyiv,

UkrЕSCO


20
Alexander Omelynsky

Deputy Chief Powerman
Mariupol

AZOVSTAL


21
Vitaly Parafeynyk

Chief Powerman
Mariupol

Illicha Plant




22
Igor Pydguyny 

Head of the Boiler House
Yamnytsa

Cement Plant


23
Alexander Razgyvin 


Malyn

Paper Plant


24
Alexander Rogachevsky


Dnipropetrovsk

ARMSTRONG


25
Igor Sery 

Chief Powerman
Kyiv

«АVIANT»


26
Volodymir Strygonov 

Chief Engineer
Donetsk

Bakery plant No.3


27
Olga Toteva

Engineer
Kyiv

ЕНВІТЕК


28
Alexander Khadgynov 

Director
Mariupol

«Energy Saving»




29
Oleg Sherbanov

Deputy Chief Powerman
Donetsk

I&S Plant


30
Alexey Yurchenko

Deputy Chief Powerman
Pology

Oil Extraction Plant


31
Lidia Yakimchuk
Kyiv

«Оrgharchprom»


32
Igor Yarynovsky
Kyiv

«Оrgharchprom»


Appendix 2

Schedule of Workshop

Alliance to Save Energy (USA)

Agency for Rational Energy Use and Ecology

ARENA-ECO (Ukraine)

SCHEDULE OF WORKSHOP

“International experience of energy efficiency improvement of generation  and consumption of heat in steam systems”.
January 18 – 19th, 2000.
First Day: 18th of January 2000

Time
Title of report, content of measure
Lecturer

9.00 – 10.00 
Registration of participants


10.00 – 10.20
Opening of workshop. Opening address.


Representatives of Alliance to Save Energy and 

the Agency for Rational Energy Use and Ecology

10.20 - 10.40
Problems of steam use in Ukraine 
Representative of 

The State Committee of Ukraine for Energy Conservation

10.40  – 11.20
Boiler houses, steam production and consumption in USA. Measures to increase energy efficiency of steam boilers.
Representative of 

Alliance to Save Energy

11.20 – 11.40
Coffee break.


11.40 – 12.20
Energy efficiency equipment in boiler houses. Combustion process. Fuel saving measures at steam production
Representative of

Alliance to Save Energy

12.20 – 13.00
Steam from CHP or from own boiler house. Estimation on investments required for boiler house upgrade. 
Representative of

Armstrong

13.00 – 13.10
Questions and answers


13.10 – 14.00
Lunch-break.


14.00 – 14.40
Energy efficient steam systems
Representative of

Armstrong

14.40 – 15.20
Videofilm “Let’s talk steam traps/update” (main types and operating principles)
Armstrong

15.20 – 15.40
Coffee break.


15.40 – 16.20
Boiler automatic control system. Burners control. Highly efficient boiler houses.
Representative of

Alliance to Save Energy

16.20 – 17.00
Measures to reduce heat consumption. Equipment for heat recovery. Economizers. 
Representative of

Alliance to Save Energy

17.00 – 17.30
Gas-and-oil fired steam boilers, their types, characteristics and equipment, produced in Ukraine.
OJSC “Tekom” Monastyrische

17.30 – 18.00
About experience of preparing and implementing investment projects in industry of Ukraine
Volodymir Laskarevskiy 

Lead expert 

Agency for Rational Energy Use and Ecology (ARENA-ECO)

18.00 – 18.30
Organization issues.


18.30 – 20.00
Reception 


Second Day: 19th of January 2000

Time
Title of report, content of measure
Lecturer

9.00 – 9.10 
Discussion of first day information.


9.10 – 9.50
Systems and units to measure gas, steam and condensate. Heat insulation of pipelines and equipment. 3Е Plus Program. 
Representative of

Alliance to Save Energy

9.50 – 10.30 
Equipment and feed water processing and monitoring methods
Representative of

Alliance to Save Energy

10.30 – 11.10
Characteristics of domestic enterprises steam systems. Energy efficient steam distribution system. Characteristics of condensate drainage with the control of steam inflow.
Representative of

Armstrong

11.10 – 11.30
Coffee break.


11.30 – 12.10
Influence of steam quality on technological process. The right way to vent condensate. Diagnostics of steam traps state. Obtaining and consumption of second boiling steam.
Representative of

Armstrong

12.10 – 12.30
Videofilm.
Armstrong

12.30 – 12.40
Questions and answers


12.40 – 13.10
Domestic equipment for feed water monitoring
(ENVITEK Kyiv)

13.10 – 14.00
Lunch break


14.00 – 14.20
Experience of steam consumption in Donezk oblast
Oleksandr Kirichok 

Chief of the oblast inspection on energy saving, Donezk city

14.20 – 14.50
Basics of process of production management and energy consumption (Energy management).
Representative of

Armstrong

14.50 – 15.20 
Enterprise energy inspection (Energy audit)
Volodymir Deriy 

Lead specialist 

Agency for Rational Energy Use and Ecology (ARENA-ECO)

15.20 – 15.35
Domestic designs for efficient steam consuming equipment. Turbine expanders.
Scientific and production enterprise “Naftagaztechnologiya”

 Sergiy Korolyov 

15.35 – 15.50
Coffee break


15.50 – 16.30
Round table. Questions and answers
Representatives of:

-State Committee of Ukraine for Energy Conservation;

-Alliance to Save Energy;

-Agency for Rational Energy Use and Ecology

16.30 – 17.00
Workshop closing


Appendix 3

Module 1: Introduction

MODULE 1: INTRODUCTION
Ukraine
· Energy intensity trend (Fig 1.1)

· Fuel prices

· Major energy consumption areas

USA
· Fuel used in manufacturing plants to produce steam (%) (Fig 1.2)

· Manufacturing energy end-use (Fig 1.3)
· Estimated unmanaged steam system efficiency improvement potential (Fig 1.4)

Economic/Technical/Market Potential

· Barriers

· Human potential gap (Fig 1.5)

Boiler Operation vs Management

· Perception:Boilers are operated not managed

· U.S. Survey: More attention to operation then managing

· Evidence: Lack of instrumentation
Boiler Energy Management Program (BEMP)

· Accountability

· Central to success of BEMP

· Energy use, not just supply

· Knowledge of spotting waste and corrective Action
Achieving Accountability: Measure and Manage

· Establish a system to collect data: Instrumentationand recording

· Interpret data: Make sense of data; identify waste; graph utility bills

· Act on the information to control losses
Key Elements of an Effective Energy Management Program:

Commitment from management

· Communication of energy savings potential

· Speak their language: Minimum Return on Investment (ROI)

Boiler System Testing

· Benchmark existing operating parameters

· Fuel data; maximum consumption rate

· Boiler hours of operation; annual fuel use, fuel unit cost

Economic evaluation and project ranking

· Life cycle costs vs first costs

Complete Energy Management Plan

· Take a long term view

· Measurement and verification

Issues/Definitions/Overview

· HHV vs LHV

· Certification of boilers

· Definitions of boiler terms: stack, burner, economizer, blowdown

· General layout of the boiler workshop

· Sheet of unit conversions

[image: image1.png]Tons O1l

Equiv/million
1980 $ GNP
900
800 Soviet Union
700 | \/
600 —
United States
500 —
OECD
400 - Countries
300 +
Japan
200 +—
| | | | ] [ |

1960 1965 1970 1975 1980 1985 1990



Fig 1.1: Energy Intensity Comparison

Fig 1.2: 
Fuel Used in Manufacturing Plants to Produce Steam (%)

1.
Forest Products: 
81% 



2.
Food Processing:
54% 



3.
Chemicals:  

46%



4.
Textiles:  


41%
5.
Petroleum:


26%

6.
Steel:  



22%

Fig 1.3:
Manufacturing Energy End-Use


Fuel Energy Input (10^9 BTU)

Sector
Process Heating
Process Cooling
Machine Drive
Facility HVAC
Lighting
Boiler fuel

1994







Food Products
192 
49 
102 
50 
13 
561 

Pulp and Paper
140 
4 
191 
28 
10 
849 

Chemicals
680 
43 
380 
38 
16 
1,229 

Petroleum
535 
6 
109 
9 
4 
304 

Steel
487 
2 
81 
29 
7 
132 









1991







Food Products
148
43
81
33
12
495

Pulp and Paper
134
3
173
10
9
796

Chemicals
621
29
342
21
15
999

Petroleum
519
5
88
14
4
318

Steel
371
1
58
21
4
111

Boiler fuel inputs comprise the greatest fuel use in Food Products, Pulp and Paper and Chemical and Chemical Industries; second greatest in Petroleum and Steel to Process Heating

Fig 1.4
Estimated Unmanaged Steam System Efficiency Improvement Potential

Generation
2-5 %

· boiler tune-ups and heat recovery
2-4%

· load controls
1-3%

· emissions monitoring
1-2%

Distribution 
12-21 %

· steam leaks
2-4 %

· steam traps
8-12%

· insulation
5 -9%

Recovery
9-14 %

· water treatment
5-6%

· condensate return
5-8 %

Total
20-30 %

Note that system efficiency is not additive, due to the interrelated nature of the parts.  Most system efficiency potential is in Distribution and Recovery

Fig 1.6: BOILER RATING & ENERGY FLOW RATE CONVERSIONS

(1 HP = .746 KW = 2.17 x 10–4 Btu/hr)

Multiply  
By
(Reciprocal Conversion) 
To Obtain

Boiler HP
34.5

(0.029)


lbs. steam/hr F&A 212F

Boiler HP
33,475

(0.0000299)

Btu/hr (output)

Boiler HP
15.64

(0.0639)

kg steam/hr F&A 100C

Boiler HP
9.81

(0.102)


KW

Boiler HP
139.5

(0.000717)

EDR sq. ft. steam radiated

Boiler HP
223


(0.000448)

EDR sq. ft. hot water radiated

Source:  Garay, 1995.  Handbook of Industrial Power and Steam Systems

The following table provides conversion factors to and from the metric quantities.
1
equals   
kJ/hr
 kW
  
  kg CE / hr    Btu/hr       kcal/hr

kJ/hr


    
 0.00028    0.000034      0.948         0.239

kW        

 3,600
    
    
  0.123
       3,412         860

HP    
       0.000229   0.746

               0.000217   0.0000547

Btu/hr    
       1.055
         0.00029
  0.000036       

         0.252
kcal/hr
       4.18
         0.00116
  0.00014
       3.97

1 petajoule (PJ) = .278 terawatt-hour (tWh) = 34.1 million kg Coal Equivalent (CE) = 0.948 Quad

Appendix 4

Module 2: Basic Overview of  Boiler Efficiency and Combustion Controls

MOD 2: BASIC OVERVIEW OF BOILER EFFICIENCY AND COMBUSTION CONTROLS

Boiler efficiency vs system efficiency

· Boiler efficiency is part of the system

· System efficiencyincludes generation, distribution, and consumption

· Keep the larger picture in mind

Starting Point For Boiler Plant Optimization is the 
As-found Efficiency:

· Is the efficiency for a boiler in its existing state of repair and maintenance

· Use as a benchmark

· Make documentation

· As-found boiler efficiency is site specific

· U.S. DOE survey Fig 2.1 and Fig 2.2 

· What we see from these figures:

· Efficiency decreases as the bottom of the turndown ratio is approached. Mixture not good at low turbulence-compensate with excess air
· At maximum firing rate-reduced “RESIDENCE TIME”

Tuned up or Baseline Efficiency

· Is the efficiency after making operating adjustments, lowering  excess air, and minor repairs have been completed.

· Baseline efficiency for estimating all future capital improvement savings

· Future savings estimates hinge on the accuracy of this number

(delete space)

Theoretical vs Technical vs Economical Efficiency

· Theoretical research level

· Technical efficiency is the goal of manufacturers

· Economic efficiency is of value to the plant managers

· There is another aspect we call the market efficiency, which is of more interest to policy makers and is concerned with institutional and structural issue

Maximum Technical Efficiency

Fuel
Rated Capacity Million BTU’s/Hr


10-16
16-100
100-250

GAS
86 %
86 %
86 %

OIL
89 %
89 %
90 %

Maximum Economic Efficiency

Fuel
Rated Capacity Million BTU’s/Hr


10-16
16-100
100-250

GAS
80 %
82 %
84 %

OIL
84 %
87 %
88 %

· Larger boilers economic efficiencies closer to technical efficiency

· Smaller boilers the techno-economic gap is 5-6 %

· Oil burns at a higher flame temperature of 4200 F so radiative heat transfer rate and efficiency is higher for oil fired burners systems

Boiler losses can be grouped in three broad areas:

· Stack losses: (excess) air and high stack temperature (most loss)

· Blowdown (second most loss)

· Surface losses(least loss)

· Stack losses

· 25 % of the boiler efficiency loss…Higher priority

· Ukraine, and FSU (Former Soviet Union?) high losses found…too much excess air

· Higher stack temperature ( poor heat transfer: soot or scale deposits Fig 2.3

· Blowdown losses

· Often overlooked-hard to measure

· Usually the losses range from 4 to 6 percent

· Rate depends on condensate recovery and water chemistry

Surface losses

· Consist Of convective and radiative losses from the boiler surface and valves and piping in the boiler plant

· Usually account for 1 To 3 Percent of total losses

· However,this loss increases as load decreases…as high as 8 % 

Combustion controls schemes:

Basic burner firing rate is controlled from steam pressure.  A master controller then sends a signal to the control system.  There are three levels of control systems available, from the most basic to the state of the art microprocessor based.  The most basic is the jackshaft control (also known as single-point control system control).  The next level is the parallel positioning, independent or multi-point control system and finally the most efficient is the metered or O2 trim system.

Jackshaft or Single-Point Control Fig 2.4:

· Mechanical linkage simultaneously controls air and fuel.

· Open control loop;no feedback loop from combustion chamber to ensure proper ratio

· Cam ratios preset, wear over time and affect the air/fuel ratio.

· Non-linear characteristics of flow control devises leads to excessair at low load conditions.

· This maybe the most common type of control scheme in Ukraine.

· An improvement over this is to eliminate the non-linear characteristics of the mechanical linkage and provide calibrated independent control devises on the air and fuel.

Parallel or Multi-Point Control Fig 2.5:

· Most common type of control used on boilers in the U.S.
· Open control loop, No feedback loop from combustion chamber to ensure proper ratio

· Employs mechanical, pneumatic, electronic and DDC based control elements

· AUTOFLAME® microprocessor based, can program it at start-up, requires calibration (due to open loop setup)

· Use only on variable boiler load applications to justify cost

The O2 trim control scheme Fig 2.6

· Incorporates feedback “closes the loop”

· See combustion chapter from steam challenge regarding O2 changes with amb temp, O2 trim can account for these changes

· Manufacturers and costs.

Burner Turndown Ratio:

· Low Turndown Ratio (inefficiency at low loads: purge cycle losses, heat transfer by combustion air from boiler up the stack)

· TDR in older US boilers is 3-4:1 the new ones have a TDR of 10:1

· For a boiler that operates at part load a fair portion of the time the savings from going to a high TDR burner can be significant.  In the neighborhood of 3 to 10 percentage point improvement in efficiency has been seen

· Experience in the FSU countries-excess air quantities adjusted manually and are usually set very high.  The control system relies on air pressure as a substitute for airflow measurement and the boiler operator has to make an airflow set point adjustment after each load change.

[image: image2.wmf]EFFECT OF SOOT ON FUEL CONSUMPTION

0

1

2

3

4

5

6

7

8

9

1/32"

1/16"

1/8"

SOOT LAYER ON HEATING SURFACE

INCREASE IN FUEL 

CONSUMPTION (%)

Fig 2.1 Source: Taplin, Fairmont Press

[image: image3.wmf]EFFECT OF SOOT ON FUEL CONSUMPTION

0

1

2

3

4

5

6

7

8

9

1/32"

1/16"

1/8"

SOOT LAYER ON HEATING SURFACE

INCREASE IN FUEL 

CONSUMPTION (%)

Fig 2.2  Source: Taplin, Fairmont Press

[image: image4.png]Tons O1l

Equiv/million
1980 $ GNP
900
800 Soviet Union
700 | \/
600 —
United States
500 —
OECD
400 - Countries
300 +
Japan
200 +—
| | | | ] [ |

1960 1965 1970 1975 1980 1985 1990



Fig 2.3 Source: Taplin, Fairmont Press

[image: image5.png]Efficiency %
86

82

78

76

30 40 50 60 70 80 90 100
% of Rated Capacity

Figure 1.1 Typical performance of Gas Fired Water Tube Boilers



Fig 2.4 Source: Taplin, Fairmont Press

[image: image6.png]76

30 40 50 60 70 80 ) 100
% of Rated Capacity

Figure 1.2 Typical performance of oil fired water tube boilers.



Fig 2.5 Source: Taplin, Fairmont Press 

[image: image7.wmf]EFFECT OF SOOT ON FUEL CONSUMPTION

0

1

2

3

4

5

6

7

8

9

1/32"

1/16"

1/8"

SOOT LAYER ON HEATING SURFACE

INCREASE IN FUEL 

CONSUMPTION (%)

[image: image8.png]steam
pressure o
signal SF o
master
pressure
controller [} ‘.
’ )
control fue! flow
signal A control valve
s o adjustable camn
a
jackshaft '
drive '

air flow
damper

v

Figure 8.4. Jackshaft burner control system.



 
Appendix 5

Module 3: Combustion Efficiency Improvements: Boiler Tune-Up/Maintenance

MOD 3: COMBUSTION EFFICIENCY IMPROVEMENTS: BOILER TUNE-UP/MAINTENANCE

Two steps to improving boiler efficiency: 

· Tune-up/maintenance, and 

· Equipment Modifications

· Reducing  excess (XS) air-most cost effective boiler efficiency improvement 

· Low cost 

· First proper maintenance and operation

· Inspecting the burner assembly 

Check to make sure that the:

· Clean: gas injection orifices, H2O traps, oil tip passages & strainers

· Reduce excessive play on air/fuel control linkages 

· Oil gun is positioned properly within the burner throat

· Right oil temperature and pressure is maintained

· Eliminate any air leakage into the boiler furnace/stack assembly

· Stack Temperature

· Stack temperature: indication of cleanliness of boiler tubes

· should ideally be in the range of 150 F – 200 F range 

· Tube fouling can be on both the fireside and the waterside: soot fouling and scale (Fig 3.1)

· Efficiency gains from stack temperature reduction: 

· Example: what will the efficiency change be with an excessair of 60 % if the stack temperature is reduced by 100 F?

· Solution: The factor from the chart at 60 % XS air is 0.325 (Fig 3.2)

 efficiency improvement: 100 F/10 * 0.325 is 3.25 %.
Boiler Tune-Up

· Chemistry of Combustion

· Stoichiometric point: Perfect combustion is the proper mixture of air and fuel under exacting conditions where both the O2 and the fuel are completely consumed in the combustion process.   Ideal combustion.

· The combustion reaction for natural gas is 

CH4 + 2O2 + 7.53N2  (  CO2 + 2H2O + 7.53N2 + 1,013 Btu/Ft3
· Below the stoichiometric point : Incomplete combustion ( CO and H2 combustibles

· Real world: stoichiometric point combustion is unattainable due to imperfect mixing, need  excess air

The fundamental rule is:

Maximum combustion efficiency is achieved when the correct amount of excess air is supplied so the sum of both unburned fuel loss and flue gas heat loss is minimized.
The relationship of CO and O2 is given by (Fig 3.3)

The question then becomes how much excessair is appropriate.

It depends on several limiting factors:

· Flame stability

· Level of CO in gas fired units known as the CO Threshold Limit 

· Smoke in the stack in oil fired units or Smoke Threshold
· Equipment-related limitations such as too low windbox/furnace pressure differential

Reducing Excess air Step by Step

1. Boiler in manual mode, set firing rate, check safety interlocks 

2. Record boiler steam pressure, load, stack temp, CO, O2 data.

(If O2 and CO level are at a minimum then go to new firing rate)

3. Reduce airflow in small increments and note:

· Any signs of smoke in stack or unstable flame operation

· Record CO or SSN readings at various O2 settings

· Record corresponding stack temperature

4. Draw the CO/O2 or Smoke/O2 curves and find the minimum excess O2 level (Fig 3.4 and Fig 3.5)

5. Set the excess air quantity - provide buffer zone

6. On boilers with independent or parallel positioning control systems repeat steps 1-5 at different firing rates. Avoid low fire rates.

7. Test the settings by imposing false loading on the boiler to see that the new burn ratio settings do not enter into an undesirable operating condition.  Reset controls as necessary.

Demo of Combustion Analyzer

· Principle components including the various sensors

· No LHV so efficiency readings lower

· Input fuel parameters: Heat content and composition

· Proper location of probe in stack

· Maintenance and calibration

· Costs.  Best way to use a combustion analyzer is to hire combustion service instead of purchase.

Estimating Energy Savings Calculations
CS  =
Wf x
 (
En-Eo
) 
x Cf  x Hr




En



CS: Energy Savings potential per year ($)

Wf: Average fuel use rate over the year (million Btu/Hr)

En: New or improved efficiency (%)

Eo: Old or Existing or As-Found efficiency (%)

Cf: Cost of fuel (per million Btu)

Hr: Average annual hours of boiler operation (hours/year)
· Efficiency improvements can be obtained from the combustion analyzer print out or corresponding efficiency improvement from stack temperature reduction can be estimate from (Fig 3.2)

· The average fuel use rate and the hours of operation multiplied also give the annual fuel consumption and this data can be obtained from utility billing information.

· The annual hours of operation can be obtained from the boiler operator.

Example: Energy savings from reducing too much Excess air-FSU plant

Example: Energy savings from tube cleaning-stack temp reduction

Example: Energy savings from optimizing multiple boiler loading
[image: image9.png]7 , may utilize pressure

é tansmitter here

master
PR pressure
controller
—p— Process piping
Pneumatic signal
P :‘:,“” —¥—%- Instrument air supply
station

Y

F— lir{fucl
ratio
controller
fuel valve
e | ositioner
Sl
3 damper
positioner
(| &=F O
S |
fuel valve
combustion
"“ air fan
c———————%)
~aY,

u‘

Figure 8.3. Pneumatic parallel positioning control system.



Fig 3.1 Source: Taplin, Fairmount Press
[image: image10.png]3

air flow

\ transmitter

air flow
sensor

pressure
transmitter
Process piping
Electronic signal
master
pressure
controller
air/fuel i i
. fuel flow
ratio . .
ansmitter
controller \! mitte
manual/ ‘
suto
station
4
! fuel valve |
| ! positioner :
Q=)
damper
positioner |
== - Tt
| Y dS }
fuel valve flow element

combustion
air fan

Figure 8.7. Metering control system.



Fig 3.2 Source: Taplin, Fairmount Press
[image: image11.png]EFFICIENCY IMPROVEMENT WITH EACH
10 F CHANGE IN STACK TEMPERATURE

0.4

0.39

0.38

0.37 4

0.36 A

0.35 /L

0.34 A

0.33 y 4

0.32

0.31 ,/
0.3 _

0.29

0.28 //

0.27 i

0.26

0.25

0.24 /

0.23 ——F

0.22 -

0.21
0.2

<O0ZM—=0O~-=TMmm

R —~HZMIM<ODIZ—

0O 10 20 30 40 50 60 70 80 90 100
EXCESS AIR (%)

Figure 4.3, Efficiency change for each 10°F change in stack temperature for various levels of
excess air.



Fig 3.3 Source: Taplin, Fairmount Press
[image: image12.png]Ip

ionsh

Efficiency

Oxygen-CO Relat

{(ppm)
1000

Carbon Monoxide CO

iency

ighest Effici

H

%

®,

%

T tee

CO Control Range

5

2% 3% 4% 5% 6% 7%

%

1

0%

-1%

Flue Gas Oxygen
Figure 9.1, CO-Oxygen relationship showing CO control

range and the effect of CO and oxygen levels on

combustion efficiency.



Fig 3.4 Source: Taplin, Fairmount Press
[image: image13.png]Combustion Efficiency
Oxygen-Smoke limit Relationship

Smoke Spot Number

5
fCurve 2

4+

Curve Operating margin .
3k (for minimum O2 Controls adjusted to

this O2 level
(-Smoke Limit >

2 -
1r Minimum O2 *
0 % : — % }
1% 0% 1% 2% 3% 4% 5% 6%

Flue Gas Oxygen

Figure 9.14. Characteristic curve identifies minimum excess air and tune-
up control settings for oil fired boilers. Curve 1 Gradual smoke/O,
relationship. Curve 2 Steep smoke/O, relationship. The type of curve is
dependent on burner operating characteristics and varies with the firing
rate and the particular type of burner.



Fig 3.5 Source: Taplin, Fairmount Press
Appendix 6

Combustion Efficiency Improvements

MOD 4: COMBUSTION EFFICIENCY IMPROVEMENTS: 
HIGH EFFICIENCY BURNER SYSTEMS AND CONTROLS AND STACK HEAT RECOVERY ECONOMIZERS

HIGH EFFICIENCY BURNER SYSTEMS AND CONTROLS

General characteristics of good control systems:

· Accurate air/fuel input measurement & control-flow measuring devices

· Correct synchronization of fuel and air input

· Consistent reliability and repeatability

· Auto trim of excess oxygen to a preset minimum under all dynamic and steady-state conditions

· Continuous optimization of the combustion efficiency despite changes in fuel Btu, ambient air temperature, and relative humidity

Modern Ways Of Achieving Better Combustion Efficiency: 

· High turndown ratio burners

· Multi-point positioning controls

· Over fire draft control

· O2 trim

· Caveat: variable load

High turndown ratio burners
· Avoid cycling losses at low loads: pre-purge & post-purge

· Ukraine TDR is 3:1 (cycle below 33% load)

· Average TDR of US Burner is 8:1

· Retrofit Issues: Furnace geometry, physical characteristics, certification issues

· Example: Energy savings potential in FSU plant

Multi-Point Positioning Controls

· Independent controls

· Repeatability improved: No mechanical linkage

· Calibrate setting at various firing rates

· Retrofit valve actuators and add controller

Overfire Draft Control

· Compensates for varying conditions

· Useful in high stacks: >40 feet

· Precursor to O2 Trim

O2 trim

· Ultimate in precise combustion control

· Feedback loop provides dynamic control: accounts for changes in environment

Boiler Economizer Heat Recovery

· Recover heat from hot stack gases

· Simple technology

· Pre-heat the feedwater

· Coincidental heat source and demand

· Boiler above 75 psig good application potential

· Paybacks usually less than two years

Acid Corrosion Concerns
· Condensation of sulfuric acids (Fig 4.1)

· Particularly oil- based fuels

· Acid dew point limit

· Worst case is cold-end connection

· 300 F lower exit gas temperature limit

Mitigating Cold-End Acid Corrosion in Economizers

Fuel Type
Minimum Inlet Water Temperature, F
Maximum Exit Flue Gas Temperature,  F

Natural Gas
210
300

No. 2 Oil
220
325

No. 5&6 Oil (Mazut)
240
350

Other Means Of Minimizing Acid Corrosion

· Stack design: Drain collar section or Off-set 

· Insulate stack metal: Raise metal skin temperature above acid dew point

· Parallel flow through the economizer: Raises pipe surface temperature on the inlet (cold-end) side

· Corrosion resistant materials: Corrosion resistant alloy steels, however costly 

· Preheating feedwater: Larger size systems (Fig 4.2)

Example: Energy savings calculations for stack economizer heat recovery

Boiler Efficiency and Management Program

These appear in the logical sequence in which boiler efficiency improvement should be approached and start with the least cost/no cost options to the energy efficiency equipment installation/investments.  

Operation and maintenance improvements

· Tube cleaning and maintenance

· Reduce air leakage

· Repair damaged insulation

· Multiple boiler load management

· Boiler tune-Up

· Combustion analysis

Technology Upgrades

· High turndown ratio burner retrofit

· Overfire draft control

· O2 trim

· Economizer heat recovery

[image: image14.png]Combustion Efficiency
Oxygen-CO Relationship

Carbon Monoxide (CO)

/Curve 2

Operating margin
for minimum 02 Controls adjusted to

< N, this O2 level

7001 Curve 1

O 1 1 T ~ = } B =
-1% 0% 1% 2% 3% 4% 5% 6%
Flue Gas Oxygen

Figure 9.15. Characteristic curve identifies minimum excess air and tune-
up control settings for gas fired boilers. Curve 1 Gradual carbon
monoxide/O, relationship. Curve 2 Steep carbon monoxide/O,
relationship. The type of curve is dependent on burner operating
characteristics and varies with the firing rate and the particular type of

burner.
11



Fig 4.1

[image: image15.png]400

300
w
e
§ 200
3
(a]
100
(Based on 25% excess air
for combustion)
0 i i 1 L 1
0 1 2 3 4 5 6

Sulfur Content of Qil (%)

Figure 12.3. The relationship of acid dewpoint to the sulfur content of fuel.



Fig 4.2

Appendix 7

Module 5: Metering Equipment and Insulation Systems

MOD 5: METERING EQUIPMENT AND INSULATION SYSTEMS

Brief Recap of the Previous Day

Operation and maintenance improvements

· Tube cleaning and maintenance

· Reduce air leakage

· Repair damaged insulation

· Multiple boiler load management

· Boiler tune-up

· Combustion analysis

Technology Upgrades

· High turndown ratio burner retrofit

· Overfire draft control

· O2 trim

· Economizer heat recovery

Role of Metering as an Energy Management Tool

· Creates awareness of energy use

· Continuous process unlike an audit

· Results in better control cnd commitment to energy efficiency

· Better energy use information helps in forecasting & decision making

· Invariably leads to reduction in energy use and cost

What to Meter?
· Steam use

· Boiler feedwater

· Fuel use

· Stack temperature

Types Of Metering Equipment:

· Steam-(1) Orifice Plate, or (2) Vortex Meter

· Natural Gas- Turbine

· Boiler Feedwater-(1) Turbine, or (2) Vortex Meter

Insulation Systems

· Basic function-retard flow of unwanted heat energy

· Minimize 3 modes of energy transfer: conduction, convection and radiation

Heat flow =
Temperature Difference


Resistance to Heat Flow

· Thermal conductivity, or k value

· Amount of heat that passes through 1 square foot of 1-inch-thick material in 1 hour when there is a temperature difference of 1 F across the insulation thickness.

k = Btu-in/hr-ft2
The lower the k value, the more efficient the insulation.
· Thermal Resistance

· Heat flow is reduced by increasing the thermal resistance

· The two types of resistances - mass and surface

· Mass for Homogeneous material

RI = thickness * 1/k

Represents total resistance to heat flow for a given thickness of material

· Surface resistance and this is defined as:

Rs = 1/f
f is the surface film coefficient

· Total resistance of the insulating system is:

Rtotal = RI + Rs
· Overall coefficient of heat transmission of the insulation system is defined as:

U =
1


RI + Rs

Important Properties of Insulating Materials

· Temperature Use-Range: On thermal systems the upper limit is important.  Physical degradation can take place gradually compromising performance.

· Degradation of thermal conductivity: some foam products lose gas additives over time and develop an “aged k” value over time, which is higher than the original value.

· Compressive Strength: Need to consider this where the insulation will experience a physical load, such as buried pipe applications.

Common Industrial Insulation Types and Properties Used in Thermal Applications

Insulation Type
Temp Range F
Thermal Conductivity at Mean Temperature Btu-in./hr-ft2-F



75 F
200 F
500 F

Glass Fiber Blankets
To 1200
0.24 – 0.31
0.32 – 0.49
0.43 – 0.73

Glass Fiber Boards
To 1000
0.22
0.28
0.51 – 0.61

Glass Fiber Pipe Covering
To 850
0.23
0.30
0.62

Mineral Fiber Blocks
To 1900
0.23 – 0.34
0.28 – 0.39
0.45 – 0.82

Protective Coating and Jackets

· Ensure proper life and performance of the insulation system especially outside

· Seen many installations in Ukraine where the insulation is damp and deteriorated

· Waterproof aluminum jacketing

3E Plus Program Demo
· Optimal Insulation thickness

· Energy savings estimate from insulation

Appendix 8

Module 6: Chemical Treatment and Blowdown Heat Recovery

MOD 6: CHEMICAL TREATMENT AND BLOWDOWN HEAT RECOVERY

Need for chemical treatment

· Hardness

· Oxygen

· Dissolvedsolids

· Alkalinity

Hardness

· Scale build-up on the heat transfer tubes-impair heat transfer efficiency 

· Calcium and magnesium are the main elements

· Ability of water to hold hardness decreases with water temperature.

· Overheating of the tubes - failure (Fig 6.1)
· Water softners: Sodium ion exchangers that zeolites
· Phosphate treatment forms sludge; phosphate residual: 30 to 60 ppm,

Oxygen

· Pitting boiler drum metal and tubes-eventual failure

· Oxygen solubility decreases with water temperature-so comes out

· Mechanical deaeration: 98 % removal of dissolved oxygen

· Chemical oxygen scavengers: sodium sulfite (NaSO3) : Sodium Sulfite residue Of 20 to 60 ppm

Dissolved Solids

· Present in the make-up water and left in the boiler by the free-leaving steam

· Accumulate at surface (Carried by steam into system: Deposit on strainers and control valves

· Top continuous blowdown 

· Level of Solids measured by conductivity

· Manual control : ( 20% of the desired dissolved solids level

· Automatic operation: ( 5%.

Alkalinity 

· Can lead to “caustic embrittlement” failure

· Proper alkalinity is maintained by adding NaOH.

Factors That Minimize Boiler Blowdown & Improve Energy Efficiency:

Minimize blowdown by manual adjustment

· Establishing operating procedure & frequent water quality testing

· Minimize blowdown by automatic adjustment (Fig 6.2)

· Average boiler plant can save about 20 percent in blowdown

· Decrease blowdown by recovering more condensate

· Essentially free of water impurities-dilutes the concentration of impurities

· Most cost effective: Save in energy and chemical costs 

· Energy efficiency improvement potential is enormous.

Estimating BD Reduction:

Percent BD =
A
* 100


(B-A)


A
= ppm of impurity in BFW 

= (Makeup water impurities in ppm * percent makeup)

B
= ppm of impurities limit in boiler drum

Example:  Say we improve the condensate recovery rate on a steam system from 50 % to 75 %, and the makeup water impurity level is 10 ppm and the boiler drum maximum allowable limit is 100 ppm.  What is the change in the BD requirements?

Solution:

A(old) =10 x (1-0.5) = 5 ppm

B(old) = 5/(100-5) = 5.3 %

A(new) = 10 x (1-0.75) = 2.5 ppm

B(new) = 2.5/(100-2.5) = 2.6 %

The BD rate can be reduced by (5.3-2.6)/5.3 x 100 = 51 %.

BD = Percent BD * lbs/hr Steam
For a 100,000 lbs/hr steam system the reduction is

BD = (5.3-2.6)/100 * 100,000 = 2700 lbs/hr

Annual boiler fuel savings from reduced blowdown rate due to condensate recovery:

ES =
BD * HR * Cp * (Tfw – Tmu)


Boiler Average Efficiency

ES
= Annual Energy Savings, Btu

BD
= Blowdown Rate, lbs/hr

HR
= Annual hours of operation, hours/year

Cp
= Heat capacity of water, Btu/lb-F-Hr.  For water this value is ~ 1.0.

Tfw
= Temperature of boiler feedwater, degree F

Tmu
= Temperature of makeup water, degree F
Increase Allowable Drum Solids Level

· It may be possible to increase the maximum allowable impurity limit

· Consult a chemical treatment specialist

Heat Recovery from Blowdown 

Example of Blowdown 2-Stage Heat recovery (Fig 6.3)

Using the example system of condensate recovery find the blowdown heat recovery potential.  We have:

Steam rate = 100,000 lbs/hr

Boiler Pressure = 200 psig

Makeup water temperature = 60 F

New rate of BD after condensate recovery = 2.6 % (note the interaction with above ECO)

Boiler efficiency = 80 %

Annual hours of operation = 4000

Fuel cost = $4/million Btu

Solution:

The first step is to calculate the flashed steam recovery amount.

% Flash steam =
Hs – Hf
* 100


Hg


Hs
= enthalpy of liquid at boiler pressure, Btu/lb

Hf
= enthalpy of liquid at flash tank pressure, Btu/lb

Hg
= latent heat of vaporization at flash tank pressure, Btu/lb
At a flash tank pressure of 5 psig (using steam tables):

% Flash steam = (362-196)/960 = 17.3 %

Flashed steam = 0.173 * 100,000 lbs/hr * (0.026) = 450 lbs/hr

The total heat of the flash steam at 5 psig (from Steam tables) = 1156 Btu/lbs

Heat saved in flashed steam = 450 lbs/hr * 1156 Btu/lb = 520,000 Btu/hr
Similarly, the blowdown or drain from the flash tank is passed through a heat exchanger and then dumped into the sewer.  The temperature of the water leaving the heat exchanger is 20 F higher then the incoming water or 80 F.  Heat recovered in the heat exchanger:

Drain rate from flash tank (blowdown rate – flash steam) = 2600 – 450 = 2150 lbs/hr

Heat of liquid leaving the heat exchanger at 80 F = 48 Btu/lb

Heat of flash tank drain liquid entering heat exchanger at 5 psig = 196 Btu/lb

Total heat recovery potential = 196-48 = 148 Btu/lb

Actual heat recovery with 0.7 heat exchanger effectiveness 

= 0.7 * 148 * 2150 lbs /hr

= 222,740 Btu/hr
Total heat recovered in 2-stages = 520,000 + 222,740 = 742,000 Btu/hr

ES = (742000 * 4000)/0.8 = 3700 million Btus

Cost savings = $4/million Btu * 3700 million Btu = $14,800 per year.
[image: image16.png]Temperature

Sensor

Temperature
Steam ¢/ Control

....... : V alve 8

From
Boiler

Feedwater
From
—ammemn Deareating

Preheater

Temperaturza
Sensor
R — H

Feedwater

To =e————
Economizer

Heater

Condensate

Y A

Deareator

Figure 12.6. Feedwater preheater used to control cold end corrosion in the economizer and acid
dew point in the stack. The steam energy used for heating is not lost as it recycles back into the

boiler as heat in the feedwater.



Fig 6.1 Source: Steam Challenge Website

[image: image17.png]Boiler steam drum

% T
Sample

Blowdown
flow control }g—D—#
valve
cooler

l — ¢ Conductivity
) cell

AN

A
NW

AN

Blowdown to blowoff
tank or heat- Q
recovery system
oO0o
Conductivity Drain
recorder-
controller

Fig. 5.21 Automated continuous blowdown system.




[image: image18.png]1500 PSI (105 kg/cm?)
120 280,000 Btu/ft'/nr
750,000 kealm?hr) 3

100

3

&

Tube Metal Temperature Increase
3 3

[=]

0 0002 0004 0008 0.008 0.010 0.012
(0) (0.005) (0.010) (0.016)(0.020) (0.025) (0.030)

Deposit Thickness, in. (mm)

Figure 2-1. Effects of boiler scale on tube metal tempera-
ture.





[image: image19.png]Boiler steam drums Fiash

process or
deaerator
Blowdown X
lines
Level
Fiash controller

tank

Makeup water
to condensate tank
or deaerator

-
|
I
) |
|
| Heat Ne Ji
—><— .

exchanger

A
To sewer
Makeup water or
ROM treatment blowoff
tank

Fig. 5.23 Typical two-stage blowdown heat-recovery system.



Fig 6.3 Source: Turner, Fairmount Press

Appendix 9

Participant Questionnaire

Participant Questionnaire

Steam Workshop Kiev 1/18-1/19/2000

1. How many boilers does your facility have _____

2. What is the capacity of your Boilers  ______ Psi  ______ metric tons/hr ______ Average load

3. Main Fuel (check one)
( Natural Gas ( Mazut ( Other __________


4. Back-up Fuel (check one) 
( Natural Gas ( Mazut ( Other __________

5. On average, how many months a year do you have to run the boiler on back-up fuel?

 ( less than 1month 
( 1 to 2 months 
( 2 to 4 months  ( > 4 months

6. Do you know the efficiency of your boiler? 
( Yes 
( No

If yes, please indicate percent efficiency _______ %

7. What areas in your opinion offer the greatest opportunities for improving your boiler efficiency? __________________________________________________________________________________________________________________________________________

8. What is the average temperature of the stack gases? _______ deg C

9. What is the level of Excess air (not oxygen) that you provide to the air/fuel mixture in the burner? (check one)

( < 20 % 
( 20-40 % 
( 40-60 % 
( 60-80 % 
( > 100%
( not sure

10. Indicate which resources you use for information on operating your boiler efficiently (where 1=use most and 5=use least):

( Boiler Operator Experience

( Guidelines from Government Agency

( Boiler Inspector

( Boiler Manufacturer’s Guidelines

( Other specify_____________________________________

11. Who is responsible for boiler water treatment at your plant?

( Boiler Operator
( Separate Department

12. How often is the water tested? (check one)

( monthly
(  2-4 months
( 4-6 months
( Once a year
( Not sure

13. List any energy efficiency measures you may have implemented in the last 5 years.

______________________________________________________________________________________________________________________________________________________________

Participant Questionnaire Evaluation

Steam Workshop Kiev, Ukraine 1/18-1/19/2000

1. Boiler parameters

#Boilers
Bar       
tons/hr

Av.load
Efficiency*
Stack t.C
Fuel

5

40/90

75/200

60/160

85

150

mazout

9

40

35/50/75
30

60

130

coke gas

6

30/100

150/220
100/160
85-88

200

coke & BFG

8

30/100

150/220
100/150
86

200

BFG

4

13

10

6-16

82-86

180-210
mazout

12

13

20

18

89

155

mazout

3

14

10

10

86

170

mazout

6

13

20

20

91-94

92-98

gas

8

14

146

20

89-91

170

gas

3

14

10

10

96

130

mazout

5

23

20

60

85

150-180
mazout

*Are these corrected to the U.S. standard? Please add a footnote about this, as you described in the report.

2. Main Fuel 
         Natural Gas - 6    mazout- 4     Other ( blast furnace, coke) -4 

3. Back-up Fuel                Natural Gas - 4    Mazut (mazout) - 6     Other -

4. On average, how many months a year do you have to run the boiler on back-up fuel?

less than 1month  -3        1 to 2 months - 2        2 to 4 months -                > 4 months –5*

*Format is confusing. Can we adjust fonts or underscore/highlight the responses so that we can tell  them apart from the questions?

5. What is the level of Excess air (not oxygen) that you provide to the air/fuel mixture in the burner? 
< 20 % -7   
20-40 % - 
40-60 % - 1
60-80 % -
> 100% -
not sure-3

6. Indicate which resources you use for information on operating your boiler efficiently (where 1=use most and 5=use least):

Boiler Operator Experience – 4,4,2,2,4,2,3 ,4 ( Average = 3.125

Guidelines from Government Agency- 3,1,1,1,2,5 ( Average = 1.83

Boiler Inspector –2,2,2,1,5,3,1 ( Average = 2.28

Boiler Manufacturer’s Guidelines – 4, 1,3,3,5,3,1,1 ( Average = 2.625

Other specify: regime instructions, inspections reports

7. Who is responsible for boiler water treatment at your plant?

Boiler Operator - 


Separate Department – 11*

Should we have a “please specify line, but we have concluded it is the water department based on….

8. How often is the water tested? 

monthly-10
2-4 months-

4-6 months-

Once a year- 

Not sure-

9. What areas in your opinion offer the greatest opportunities for improving your boiler efficiency? 

· automatical control  of gas/fuel ratio

· flue gas analyzer 

· retrofit

· improving combustion efficiency

· boiler turn-up

· metering system

· combustion control/monitoring

· burners improvement

10. List any energy efficiency measures you may have implemented in the last 5 years.

· boiler leakages reduction 

· installation of turboblowers electrical drives

· local heating by hot water instead of steam

· installation pump drives 

· natural gas meters 

· ultrasonic unit for waste water measuring

· boiler heating surfaces cleaning

· utilization of the flash steam heat

· steam traps

· flash steam utilization

· steam pipes insulation

· economizer installations 

· pressure control system

· air pre-heater installation

· heat exchanger installation

· mazout *preheaters utilizing  flash steam

· *please keep spelling consistent.

*****




� EMBED Word.Picture.8  ���





� EMBED Excel.Sheet.8  ���





Fig 2.6 Source: Taplin, Fairmont Press








� EMBED Excel.Sheet.8  ���





Fig 6.2 Source: Turner, Fairmount Press








PAGE  
2

_1008942923.doc
[image: image1.png]Tons O1l

Equiv/million
1980 $ GNP
900
800 Soviet Union
700 | \/
600 —
United States
500 —
OECD
400 - Countries
300 +
Japan
200 +—
| | | | ] [ |

1960 1965 1970 1975 1980 1985 1990















_1008799890.xls
Chart2

		1/32"

		1/16"

		1/8"



SOOT LAYER ON HEATING SURFACE

INCREASE IN FUEL CONSUMPTION (%)

EFFECT OF SOOT ON FUEL CONSUMPTION

2

4.5

8.5



Sheet1

		1/32"		2

		1/16"		4.5

		1/8"		8.5





Sheet1

		



SOOT LAYER ON HEATING SURFACE

INCREASE IN FUEL CONSUMPTION (%)

EFFECT OF SOOT ON FUEL CONSUMPTION



Sheet2

		





Sheet3

		






